## Slide 1
www.intertech.com.co
Providing Earthing for
INTER-TECH

## Slide 2
TOPICS FOR DISCUSSION
1
Objective of Earthing
Earthing Design Inputs
Earth Enhancement Material
2
3
4
5
Common Mistakes & Do’s and Don’t
Marconite in Power and Solar Sector
6
7
www.intertech.com.co
INTER-TECH
8
Question & Answer
Advantage of MARCONITE Earth Enhancement Material
Myths & Misconceptions

## Slide 3: Objective of Earthing
Ensuring Safe Operation of Power System.
Ensuring Safety of Machine & Men.
Eliminating Electrostatic Accidents.
Reducing Electro Magnetic Interference
www.intertech.com.co
INTER-TECH

## Slide 4
www.intertech.com.co
INTER-TECH
Earth Enhancing / back fill materials in use :
Charcoal and Salt, Sodium Carbonate, Calcium Carbonate,
Calcium Sulphate, Copper Sulphate, Bentonite.
Sodium Carbonate
Calcium Carbonate
Copper Sulphate
Calcium Sulphate
Charcoal & Salt
Sodium Bantonite

## Slide 5
www.intertech.com.co
INTER-TECH
Bentonite Earth Enhancement Material?
                Bentonite is now used as a general name for water absorbing clay which usually contains mostly montmorillonite.

## Slide 6
www.intertech.com.co
INTER-TECH
Electrically Conductive Aggregate
New Earth Enhancement Material

## Slide 7
Conductive Concrete - Marconite
Carbon = Highly Conductive even in dry state Cement- Non-Corrosive and stable (Granules form)
Carbon + Cement= Conductive Concrete = Highly conductive and Non-corrosive.
Marconite is Engineered and Manufactured Product
www.intertech.com.co
INTER-TECH

## Slide 8
www.intertech.com.co
INTER-TECH
Marconite an earth enhance material was developed by Marconi company in UK, Company setup by Guglielmo Marconi, Nobel Prize winner for wireless telephony.
Marconite is an engineered product unlike the Bentonite/ Chemical earthing which is simply a natural clay
Where other product fails, Earthing specialist rely upon Marconite

## Slide 9
Very fine powder for making excellent surface contact.
Resistant to Corrosion,
Environmentally safe.
pH Inert
Mechanically Strong
Conductive Concrete Marconite as Earth Enhancing Material
www.intertech.com.co
INTER-TECH

## Slide 10: Advantage of Marconite Over Chemical Earth Enhancement Material
www.intertech.com.co
INTER-TECH
Chemical Leach away and
Non Polluting
Pollute Surrounding Soil

## Slide 11
www.intertech.com.co
INTER-TECH
Advantage of Marconite Over Chemical
Earth Enhancement Material
Chemical Earthing
Moisture Required for Recharging
Marconite Earthing
No recharging required

## Slide 12
www.intertech.com.co
INTER-TECH
Impact of Corrosion
Chemical Earthing
Corrosion after 6-8 years
Marconite Earthing
No Corrosion for 50+ years

## Slide 13
www.intertech.com.co
INTER-TECH
Chemical Earthing
Earthing Material crack/ shrink due to temperature rise
Marconite Earthing
Earthing Material does not crack/ shrink due to temperature rise
Advantage of Marconite Over Chemical
Earth Enhancement Material

## Slide 14
www.intertech.com.co
INTER-TECH
Tests at CPRI, Bangalore
Fault Current
40 mm & 100 mm Dia X 3 m – 80.52 kA
16 mm & 80 mm Dia X 3 m – 39.66 kA

## Slide 15
www.intertech.com.co
INTER-TECH
Re-locatable Electrodes for Communication lorries

## Slide 16
5kg of WOOD equals to 1KG of CHARCOAL
Wood
Charcoal
www.intertech.com.co
INTER-TECH
Requirement of Wood as Charcoal in Conventional Earthing

## Slide 17: Water Requirement
Marconite Earthing doesn’t Require Water
For Life Time
www.intertech.com.co
INTER-TECH

## Slide 18: Marconite a Green Earthing :
No requirement of Water
Charcoal earthing harms Trees
No Leaching therefore no Soil Pollution
Chemically Inert
www.intertech.com.co
INTER-TECH

## Slide 19
Soil resistivity
Required Resistance Values
Earth Enhancing Material
Design of Earthing System
www.intertech.com.co
INTER-TECH

## Slide 20
IS: 3043 : 1966, 1987 reaffirmed 2006 Code of Practice for Earthing.
Indian Electricity rules 1956 (as amended up to 2000)
IS: 2309 1989 (reaffirmed 2005) Protection of Buildings and allied Structures against lightning – Code of Practice.
IS : 2689: 1989 (reaffirmed March 2010): Guide for Control of Undesirable static Electricity.
Manual on Earthing of AC Power Systems : CBIP Publication No.302 : 2007 and 311
BS: 7430 : 1998, Code of Practice for Earthing.( formerly CP 1013: 1965) British Standard Institution London 1992
BS: 6651: 1992, Protection of Structures. Against Lightning.
IEEE :80 : 2000( Revision of IEEE Std 80: 1986) Guide for Safety in AC Substation Grounding
IEEE :142 :2007(Revision of IEEE Std 142 :1991) Grounding of Industrial and Commercial Power System.
IEEE 1100 : 2005 (Revision of IEEE Std 1100 : 1999) Powering and Grounding Electronic Equipment
Earthing Standards
www.intertech.com.co
INTER-TECH

## Slide 21
The earth resistance shall be as low as possible and shall not exceed the following limits
Power stations (Gen Stn) 0.5 ohms
EHT Sub/ Stn 1.0 ohms
33 KV Sub/Stn 2.0 ohms
Distribution Xformer ) Structure 5.0 ohms
Tower Foot Resistance 10.0 ohms
US AID INDIA Book Page 92 – Modernisation of power distributions
Maximum Accepted Earth Resistance
www.intertech.com.co
INTER-TECH

## Slide 22
Typical Soil Resistivity Values
www.intertech.com.co
INTER-TECH

## Slide 23: Relationship Soil Resistivity & Corrosion
www.intertech.com.co
INTER-TECH

## Slide 24
Type of the soil.
Moisture.
Dissolved salt in water.
Temperature.
Grain size and its distribution.
Seasonal variation.
Artificial treatment.
Factors Affecting the Soil Resistivity
www.intertech.com.co
INTER-TECH

## Slide 25: Relationship between Earth Resistance & Soil Resistivity
www.intertech.com.co
INTER-TECH
Earth Resistance Value is
Directly Proportional to Soil Resistivity

## Slide 26: Typical Example of Relationship of Soil Resistivity to Achieve ER = Less than 1 Ohm
www.intertech.com.co
INTER-TECH
Example 1.
IAF Palam, New Delhi
Installed on - 14 December 2012
Length of Electrode -
ER Achieved – 0.76 Ohm
Signed by – Ajay Sharma, Major, Garrision Enginer
Example 2.
Prasar Bharti, New Delhi
Installed on - 08 December 2012
Length of Electrode –
ER Achieved - 0.76 Ohm
Signed by – Jitendra Sarswat, AE, DDG (E)
30 Meters
4.5 Meters

## Slide 27
www.intertech.com.co
INTER-TECH
Soil pH Map of India

## Slide 28: Spacing between the 2 Earth Pits
www.intertech.com.co
INTER-TECH

## Slide 29: Sphere of Influence
Effective resistance areas (no overlapping with properly spaced rods)
Effective resistance areas (overlapping when rods are not properly spaced)
8 ft
20 ft
www.intertech.com.co
INTER-TECH

## Slide 30: Spacing between the Multiple Earth Pits
No. of Rods | Spacing Factor
2 | 1.16
3 | 1.29
4 | 1.36
8 | 1.68
12 | 1.80
16 | 1.92
20 | 2.00
24 | 2.16
www.intertech.com.co
INTER-TECH

## Slide 31
No. of Rods | Spacing Factor
2 | 1.16
3 | 1.29
4 | 1.36
8 | 1.68
12 | 1.80
16 | 1.92
20 | 2.00
24 | 2.16
www.intertech.com.co
INTER-TECH
Example 1:-
= Ohms
= 5 Ohms
Spacing between the Multiple Earth Pits

## Slide 32
No. of Rods | Spacing Factor
2 | 1.16
3 | 1.29
4 | 1.36
8 | 1.68
12 | 1.80
16 | 1.92
20 | 2.00
24 | 2.16
www.intertech.com.co
INTER-TECH
Example 1:-
= x 1.16
= 5 x 1.16 Ohms
= 5.8 Ohms
Spacing between the Multiple Earth Pits

## Slide 33: MYTHS & MISCONCEPTIONS
www.intertech.com.co
INTER-TECH

## Slide 34: MYTH : Ground Resistance of Copper Electrode is better than Steel Electrode.
Calculation of Ground Resistance for rod / pipe electrode
Fact: Ground resistance depends upon the resistivity of the soil and dimension of the electrodes.
Material used for the electrode has no role.
www.intertech.com.co
INTER-TECH
=
Where ρ = Resistivity of soil is ohm meter
L = Length of rod in cm
d = dia of rod in cm
R = Resistance in Ohms

## Slide 35
Considering ρ = 100 Ω-m, l = 300 cm, d = 4 cm
                Ω
Considering ρ = 100 Ω-m, l = 300 cm, d = 8 cm
                Ω
Myth Increased Dia Reduces Resistance
www.intertech.com.co
INTER-TECH

## Slide 36
Change in Resistance between 40 mm & 80 mm diameter pipe/rod is
= x 100 = 12.16 %
OBSERVATION:
  Doubling the diameter decreases the Ground resistance by 10 to 12%
Myth Increased Dia Reduces Resistance
www.intertech.com.co
INTER-TECH

## Slide 37
Considering ρ = 100 Ω-m, l = 100 cm, d = 4 cm
  Considering ρ = 100 Ω-m, l = 200 cm, d = 4 cm
FACT - Length Reduces the Resistance Value
www.intertech.com.co
INTER-TECH

## Slide 38
Considering ρ = 100 Ω-m, l = 300 cm, d = 4 cm
FACT - Length Reduces the Resistance Value
www.intertech.com.co
INTER-TECH

## Slide 39
Change in resistance when the length is doubled
Change in resistance when the length is increased to 3 mtr
OBSERVATION:
- By doubling the length resistance decreases by 40%
- By trebling the length resistance decreases by 60%
FACT - Length Reduces the Resistance Value
www.intertech.com.co
INTER-TECH

## Slide 40: MYTH: More water in the earth pit reduces the Ground resistance
Ground resistance depends upon the soil resistivity at a location.
Moisture is one of the factors that reduces the earth resistivity
Presence of moisture helps in decrease in earth resistance.
But this has the limit as shown in the curve. It is upto 20% moisture.
www.intertech.com.co
INTER-TECH

## Slide 41
Effect of Salt on Soil resistivity
It can be seen from the diagram the curve flattens at 5% of salt in moisture
Further increase in soil content will give less impact to decrease the soil resistivity
The salt content is expressed in % by weight of moisture content in soil
www.intertech.com.co
INTER-TECH

## Slide 42
Effect of Salt on Soil resistivity
Considering 1 cubic mtr of soil, the moisture content is 10% i.e. 144Kg. (10 % of 1440Kg of soil).
The salt content should be 5% of 144Kg i.e. 7.2Kg.
So, further addition of salt will have no impact
www.intertech.com.co
INTER-TECH

## Slide 43: Effect of soil temperature on soil resistivity
Temperature also has an effect on soil resistivity
Effect is Predominant at or near zero degree celsius
www.intertech.com.co
INTER-TECH

## Slide 44
www.intertech.com.co
INTER-TECH
Techno Commercial Comparison of Marconite V/s Bentonite
Property | Bentonite | Marconite
Resistivity | 2.5 – 5.5 Ω m | 0.001 Ω m
Maintenance Recharge of Water/ Backfill | Yes | No
Materials pH | 9-10 Alkaline | 6.9 Inert
Corrosion impact of Backfill on conductor | Yes | No Green Product
Per Year Corrosion impact on conductor | 0.0028 mm Per Year | 0.0010 mm Per Year
Leaching/ Shrinkage/ Cracks | Yes | No

## Slide 45
www.intertech.com.co
INTER-TECH
Property | Bentonite | Marconite
Corrosion impact of surrounding soil on earth enhancement material | Yes | No
Non-Polluting/ Environment Friendly | No | Yes
Deeper Installation | No | Yes
Performance Consistency for Life cycle | No | Yes
Conduction | Ionic (Presence of Water) | Electronic (Movement of Electrons)
Techno Commercial Comparison of Marconite V/s Bentonite

## Slide 46
www.intertech.com.co
INTER-TECH
Description | Bentonite | Marconite
Plant Life | 50 Years | 50 Years
Life Cycle of Earthing | 6-8 Years | 50+ Years
Replacement Frequency During Plant Life | 6 Times | 1 Times
Initial Cost (in Soft Soil) | 8,000/- | 16,500/-
Total Cost | 8,000 x 6 = 48,000 | 16,500 x 1 = 16,500
Maintenance Cost cost | 20,000 | Nil
Total Life cycle Cost | 68,000 | 16,500
Techno Commercial Comparison of Marconite V/s Bentonite

## Slide 47: Marconite Installations
www.intertech.com.co
INTER-TECH

## Slide 48
www.intertech.com.co
INTER-TECH
Marconite Customers in India

## Slide 49
www.intertech.com.co
INTER-TECH
MARCONITE IN USE AT UTILITIES
NEW DELHI MUNICIPAL COUNCIL
11 kV S/stn - Chanderlok Building, Janpath
11 kV S/stn – Rohit House, Tolstoy Marg
33kV S/stn – Bapu Dham, Dhaula Kuan (Rocky Area)
RAJASTHAN VIDYUT VITRAN NIGAM LIMITED
220 kV GIS S/stn – Nalagarh Power House, Jaipur
220 kV GIS S/stn – MNIT, Jaipur
KERALA STATE ELECTRICITY BOARD (ALL SUB-STATIONS IN ROCKY AREA)
66 kV S/stn – kochupumpa – Distt Pathanamithitta
110 kV S/stn – Enathu – Distt Pathanamithitta
110 kV S/stn – Varkala – Distt Trivandrum
110 kV S/stn – Mevlikara – Distt Allepy

## Slide 50
www.intertech.com.co
INTER-TECH
MARCONITE IN USE AT UTILITIES
MAHATRANSCO MUMBAI (ROCKY AREA)
110 kV S/stn – Roha
100 kV S/stn – Dombivili
KARNATAKA POWER TRANSMISSION CORPORATION LIMITED (ROCKY AREA)
700 mW Thermal Power Station – Baillari (Rocky Area)
UP POWER CORPORATION LIMITED, LUCKNOW (ROCKY AREA)
400 kV ESS – Chappartalla, Allahabad
CHATTISGARH STATE POWER TRANSMISSION CORPORATION LIMITED (ROCKY AREA)
132 kV S/Stn – Dallirajhara

## Slide 51
www.intertech.com.co
INTER-TECH
MARCONITE IN USE AT UTILITIES
BSES – RAJDHANI POWER LIMITED (RELIANCE POWER)
66 kV S/stn – Nangloi, Delhi
66 kV S/stn – Sangum, Delhi
66 kV S/stn – SEA University, Vasant Kunj
66kV S/stn - Dwarka, Delhi
BHUTAN POWER CORPORATION (ROCKY AREA)
66 kV S/Stn – Thimpu, Bhutan
MEIL (Western UPPCL, Hapur)
765 kV S/Stn- Hapur (Under Exceution)

## Slide 52
www.intertech.com.co
INTER-TECH
MARCONITE IN USE IN TRANSMISSION NETWORK
PGCIL - 220 KV D/C ALIPURDUAR- SALAKATI
PGCIL - 400/220/132 KV GIS S/S – RANGPO

## Slide 53
www.intertech.com.co
INTER-TECH
Roof Top- Solar Plants
750 kW Akal University, Bhatinda
1500 kW 40 Akal Academies, Punjab
108 kW Radaur, Haryana
75 kW Mukund Lal Public School, Yamuna Nagar
85 kW ICICI Bank Ltd, Noida

## Slide 54
www.intertech.com.co
INTER-TECH
22 MW Haldiram
1.6 MW DS Group
6 MW Renew Power- Nagarjuna cement
Ground Mounted Projects - In Pipe line
145 MW NTPC, Ramagundam, Telangana

## Slide 55
www.intertech.com.co
INTER-TECH
Ground Mounted Projects - In Pipe line
22 MW – Renew Power, Cumbum
30 MW MULKANOOR, Telangana
143 MW DACHPALLI, Telangana
640 MW Bikaner, Rajasthan

## Slide 56: Hospitals
Apollo Hospital, Delhi
Saral Diagnostic Lab, Delhi
Saket City Hospital, Delhi
Venketeshwar Hospital, Delhi
RR Hospital, Delhi Cantt, Delhi
www.intertech.com.co
INTER-TECH

## Slide 57: Industries
www.intertech.com.co
INTER-TECH
Dr Oetker India, Bhiwari
CIPLA Ltd., Maharshtra
Dalmia Cement, Gurgaon
Ambuja Cement
Dalmia Cement, Maharshtra
Indian Oil Refineries, Panipat
Bhushan Steel Ltd., UP (Now TATA Steel BSL)

## Slide 58: Power Sector
CSPTCL, Bhilai
Torrent Power, Agra
Zesco, Lusaka, Zambia
Adani Power, Ahmadabad
DDL – Tata Power, New Delhi
Ballary Thermal Power Station, Ballary
Karnataka Power Corp. Ltd., Bangalore
NDMC 33 kV ESS Bapudham, New Delhi
KSEB ltd 66 kV ESS at Kochupampa, Kerala
Maha Transco 100 kV ESS Roha, Maharashtra
RRVPNL 220 kV GIS Nala Power House, Jaipur
www.intertech.com.co
INTER-TECH

## Slide 59: Defence
GE (North) Af Palam, New Delhi
CWE (Utility) Mes, Delhi Cantt.
HQ 5 Signal Group, New Delhi
Rafale Training Centre, Hasimara
Rafale Training Centre, Ambala
Cod, Delhi Cantt
MCTE, Mhow
Dr Oetker India, Bhiwari
www.intertech.com.co
INTER-TECH

## Slide 60
www.intertech.com.co
INTER-TECH
We have installed Pan India
30000 + Marconite Earth Pits
Where 'No’ maintenance or Water
is required for the Next 50 years

## Slide 61
www.intertech.com.co
INTER-TECH
Chart: 
| 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
 | 3 | 39 | 58 | 95 | 107 | 141 | 153 | 235
Year Wise cumulative growth of Installation of Marconite Electrodes at TATA Steel BSL Ltd.

## Slide 62
www.intertech.com.co
INTER-TECH
Chart: 
| 2013 | 2015 | 2017 | 2018 | 2020 | 2020
 | 1 | 3 | 7 | 10 | 12 | 18
Year Wise cumulative growth of Installation of Marconite Electrode at Apollo Hospital

## Slide 63
EARTHING
EARTHING
Replacement every 7-8 years
Life Cycle of Solar Plant - 25 Years
www.intertech.com.co
INTER-TECH
Managed by O&M
Warranted by manufacturer
Warranted by manufacturer
SOLAR MODULE
INVERTER
BOS
5 Years
10 Years
15 Years
20 Years
25 Years
EARTHING
Marconite Performs for 25+ Years without water
Marconite with life cycle of 25+ Years

## Slide 64
www.intertech.com.co
INTER-TECH
Chart: 
| LAND | INVERTER | ECACATION | BOS | EARTHING | PV MODULE
Sales | 9 | 11 | 15 | 13 | 4 | 65
Where does your investment go?
General Breakup of your Investment is

## Slide 65
www.intertech.com.co
INTER-TECH
Chart: 
| LAND | INVERTER | ECACATION | BOS | EARTHING | PV MODULE
Sales | 9 | 11 | 15 | 13 | 4 | 65
Where does your investment go?
General Breakup of your Investment is

## Slide 66
www.intertech.com.co
INTER-TECH
Chart: 
| LAND | INVERTER | ECACATION | BOS | EARTHING | PV MODULE
Sales | 9 | 11 | 15 | 13 | 4 | 65
Where does your investment go?
General Breakup of your Investment is

## Slide 67
www.intertech.com.co
INTER-TECH
Chart: 
| LAND | INVERTER | ECACATION | BOS | EARTHING | PV MODULE
Sales | 9 | 11 | 15 | 13 | 4 | 65
Where does your investment go?
General Breakup of your Investment is

## Slide 68
www.intertech.com.co
INTER-TECH
Chart: 
| LAND | INVERTER | ECACATION | BOS | EARTHING | PV MODULE
Sales | 9 | 11 | 15 | 13 | 4 | 65
Where does your investment go?
General Breakup of your Investment is

## Slide 69
www.intertech.com.co
INTER-TECH
Chart: 
| LAND | INVERTER | ECACATION | BOS | EARTHING | PV MODULE
Sales | 9 | 11 | 15 | 13 | 4 | 65
Where does your investment go?
General Breakup of your Investment is

## Slide 70: Common Mistakes in Earthing
Not measuring/understanding soil resistivity
Improper design
Lesser spacing between the earth pits
Non periodical inspection
Improper spacing from the nearby wall
www.intertech.com.co
INTER-TECH

## Slide 71: Do’s
Inspect earth electrode, once in a year and clean terminal and apply rust preventive spray
Ensure terminal of earth electrode is properly cleaned of corrosion before any Measurement is taken
Ensure good and reliable electrical connection between earthing terminal leads and application
www.intertech.com.co
INTER-TECH

## Slide 72: Don’ts
Don’t locate any element like power cable, underground tank, rain water drain or another earth pit etc. in sphere of influence of existing earth electrode.
Don’t put any water or chemical in marconite earth pits.
Don’t take measurement while earthing is connected to an application.
www.intertech.com.co
INTER-TECH

## Slide 73: Managing values of desired resistance
it was also observed in some installations that the earth pit is filled to the top with salt and charcoal (this too, just days before the Electrical Inspector is due to arrive for inspecting the installation). This is a wrong practice.
If the moisture content is already above 20 percent, there is no point in adding barrels of water into the earth pit, except perhaps wasting an important and scarce national resource like water.
www.intertech.com.co
INTER-TECH

## Slide 74
Measure Soil Resistivity
Design as per desired resistance values
Ensure proper spacing between rods and nearby walls.
Periodic check of resistance values
Conclusion- Ensuring a good Earthing system
www.intertech.com.co
INTER-TECH

## Slide 75
www.intertech.com.co
INTER-TECH
Value Added Solution by INTER-TECH

## Slide 76: Recent Projects
www.intertech.com.co
INTER-TECH
Material for 6000 Earthings for 650 mW Solar Plant in Bikaner
765 kV Switch Yard at UPPTCL, Hapur

## Slide 77
www.intertech.com.co
INTER-TECH
Performance Warranty
» Installation Date : 04/2019
» Performance
Warrantee upto : 04/2044
» Earth Pit No :
» Resistance Value :
» Reading Date :
» Next Reading on :
*No Water *No Recharge
Rafale Training Centre, IAF Ambala
50+ Years Life Cycle
» Installation Date : 08/2019
» Performance
Warrantee upto : 08/2044
» Earth Pit No :
» Resistance Value :
» Reading Date :
» Next Reading on :
*No Water *No Recharge
JASOLA METRO
50+ Years Life Cycle

## Slide 78
www.intertech.com.co
INTER-TECH
Testimonials
We adopted Marconite conductive Concrete Technology for around 100 nos treated earth pits in rocky soil and we could achieve the desired earth resistance as per our client’s requirement.
G. Eyathirajulu,
Sr Manager Electrical & CI
The performance report of earth electrode encased in Marconite conductive concrete was measured and was found to be 1.84 Ohms which is satisfactory.
S M Naik,
Sr. Maintenance Manager (Electrical)

## Slide 79
www.intertech.com.co
INTER-TECH
Marconite conductive concrete is used for our Electron Beam Centre, Navi Mumbai network to achieve earth pit resistance of 0.65 Ohms. We are glad to get these maintenance free earthing station having less than 1 Ohms.
RI Bakhtsingh,
Scientific Officer (Electron Bea Centre)
KSEB installed 70 electrodes at its kochupampa 66 kv substation in rocky terrain. The earth resistance measured after 3 weeks of installation was 0.8 ohms which was earlier more than 50 ohms.
Executive Engineer
Kochupampa Substation,
Kerala State Electricity Board
.
Testimonials

## Slide 80
www.intertech.com.co
INTER-TECH

## Slide 81
www.intertech.com.co
INTER-TECH
Channel Partners of
INTER-TECH
in India

## Slide 82
www.intertech.com.co
INTER-TECH
Provides you Earthing for
Where other materials fail,
Earthing specialists rely upon

## Slide 83
www.intertech.com.co
INTER-TECH